## pl-P_water_calc_worksheet-date-
WATER CALCULATION WORKSHEET FOR: Project Name, Job Number, City, State
Date Designer
BUILDING INFORMATION
1. | Demand of building in gallons per minute (65 SFU). |  |  | 33 | gpm
2. | Size of the water meter. (Proposed size for hydraulic calcs, subject to Water Utility review.) |  |  | 1.5 | inch
3. | Low pressure at building entrance. |  |  | 35 | psi
CALCULATE PRESSURE AVAILABLE AFTER BUILDING CONTROL VALVE
4. | Low pressure at building entrance. |  |  | 40 | psi
5. | Pressure loss due to water meter. |  |  | 2 | psi
|  |  |  | #REF! | psi | (Subtract 7a & 7b from line 6.) subtotal
6. | Available pressure after building water meter. |  | (Line 6 - 7a - 7b - 8) | 38 | psi
CALCULATE PRESSURE AVAILABLE FOR UNIFORM LOSS (VALUE OF “A”)
B. | Available distribution pressure. |  | (Line 9 + B1 - B2) | 38 | psi
D. | Pressure required at controlling fixture. (Shower in second floor bathroom.) |  |  | 20 | psi
|  |  | Subtotal | 18 | psi
E. | Head loss from the building control valve to the controlling fixture.
(Elevation change, multiply by 0.434 psi/ft.)
| Elevation change ft | 25 |  | 10.85 | psi
|  |  | Subtotal | 7.15 | psi
F. | Pressure loss due to water treatment devices, instantaneous water heaters,
backflow preventers, and other accessories which serve the controlling fixture.
| N/A |  |  | 0 | psi
|  |  | Total Available Pressure | 7.15 | psi
G. | Actual pipe length from building control valve to controlling fixture ft | 80
| Developed length. (Actual length, multiply by fitting/loss factor.) | fitting/loss factor | 1.5 | 120 | feet
| Pressure available for uniform loss. (Total Available Pressure / Developed Length.) |  |  | 0.059583 | psi/ft
| Pressure available for uniform loss per 100 ft. (Multiply by 100 / 100.) |  |  | 5.9583 | psi/100 ft
A. | Pressure available for uniform loss per 100 ft. (Value rounded up to next integer.) |  | “A” = | 6 | psi/100 ft