## pl-P_water_calc_worksheet-date-
WATER CALCULATION WORKSHEET FOR: Project Name, Job Number, City, State
Date Designer
BUILDING INFORMATION
1. | Demand of building in gallons per minute. (xxx SFU/xx gpm current, xxx SFU/xxx gpm future.) |  |  | 58 | gpm
2. | Rise in elevation from hydrant to building control valve. (Negative value indicates elevation drop.) |  |  | 15 | feet
3. | Size of the water meter. (Proposed size for hydraulic calcs, subject to Water Utility review.) |  |  | 1.5 | inch
4. | Length of service from main to building control valve. |  |  |  | feet
5. | Low pressure at hydrant elevation. (Hydrant flow test dated xx/xxx/2011.) |  |  |  | psi
CALCULATE PRESSURE AVAILABLE AFTER BUILDING CONTROL VALVE
6. | Low pressure at hydrant elevation. (Value from 5. above.) |  |  | 0 | psi
7a. | Water service loss. (Pipe diameter is xx inch, material is K-copper/PVC/ductile iron, multiply pressure loss by value from 4. above, divide by 100.)
| Pressure loss psi/100ft |  |  | 0 | psi
7b. | Pressure loss due to exterior water meter (x.x psi) and exterior RPZ (xx.x psi - 8 to12 psi). |  |  |  | psi
|  |  |  | 0 | psi | (Subtract 7a & 7b from line 6.) subtotal
8. | Determine pressure loss (gain) due to rise (drop) in elevation.
| (Value from 2. above, multiply by 0.434 psi/ft.) |  |  | 6.51 | psi
9. | Available pressure after building control valve. |  | (Line 6 - 7a - 7b - 8) | -6.51 | psi
CALCULATE PRESSURE AVAILABLE FOR UNIFORM LOSS (VALUE OF “A”)
B1. | Booster pump pressure increase. (Enter zero if not applicable.) |  |  |  | psi
B2. | Water pressure reducing valve pressure decrease. (Enter zero if not applicable.) |  |  |  | psi
B. | Available distribution pressure. |  | (Line 9 + B1 - B2) | -6.51 | psi
C. | Pressure loss due to interior water meter (x.x psi) and building interior RPZ (xx.x psi - 8 to12 psi). |  |  |  | psi
|  |  | Subtotal | -6.51 | psi
D. | Pressure required at controlling fixture. (Eyewash 30/35 psig, room xx.) |  |  |  | psi
|  |  | Subtotal | -6.51 | psi
E. | Head loss from the building control valve to the controlling fixture.
(Elevation change, multiply by 0.434 psi/ft.)
| Elevation change ft |  |  | 0 | psi
|  |  | Subtotal | -6.51 | psi
F. | Pressure loss due to water treatment devices, instantaneous water heaters,
backflow preventers, and other accessories which serve the controlling fixture.
| (List devices, if any, e.g., thermostatic mixing valve.) |  |  |  | psi
|  |  | Total Available Pressure | -6.51 | psi
G. | Actual pipe length from building control valve to controlling fixture ft
| Developed length. (Actual length, multiply by fitting/loss factor.) | fitting/loss factor | 1.5 | 0 | feet
| Pressure available for uniform loss. (Total Available Pressure / Developed Length.) |  |  | #DIV/0! | psi/ft
| Pressure available for uniform loss per 100 ft. (Multiply by 100 / 100.) |  |  | #DIV/0! | psi/100 ft
A. | Pressure available for uniform loss per 100 ft. (Value rounded up to next integer.) |  | “A” = | #DIV/0! | psi/100 ft
Note on A1: Do not delete. AutoTableDXF requires this comment. If you need to add your comment to this cell, please cut and paste this comment to another cell. 80E29E48-D559-4978-B11E-5ED9FC6BC36C D:\OneDrive\03-Projects\OpenDesign\Vacation_Rental\pl-P_water_calc_worksheet-date-.dxf*pl-P_water_calc_worksheet-date-*