## Heat loss _The Downtowner
Level | Space name | Area (sq.ft ) | Volume ( cu.ft) | Occupancy | Exposed Wall |  | window |  | Partition wall |  | Floor |  | Roof exposed |  | Heat loss by wall | Heat loss by window | Heat loss by partition wall | Heat loss by Roof | Heat loss by Floor | Total Envelop Load | Infiltration @ 0.035 cfm/sft | Heat loss by Infiltration |  |  | Safety | Total Room SH with safety | Total room LH with safety | Room Total load | Design Air Quantity | Ventilation 7.5cfm/person | Heat loss by Ventilation |  |  | Total Sensible Load | Total Latent Load | Total Heat loss
|  |  |  | Nos | Net Area (sq ft ) | U (Btu/h °F ft2) | Area (sq ft ) | U (Btu/h °F ft2) | Area (sq ft ) | U (Btu/h °F ft2) | Area (sq ft ) | U (Btu/h °F ft2) | Area (sq ft ) | U (Btu/h °F ft2) | Btu/Hr | Btu/Hr | Btu/Hr | Btu/Hr | Btu/Hr | Btu/Hr | CFm | SH Btu/Hr | LH Btu/Hr | TH Btu/Hr |  | Btu/Hr | Btu/Hr | Btu/Hr | CFM | CFM | SH Btu/Hr | LH Btu/Hr | TH Btu/Hr | Btu/Hr | Btu/Hr | Btu/Hr
1st floor | Bed Room 1 | 119 | 1094.8 | 2 | 101.29 | 0.0526 | 9.11 | 0.3 | 193.2 | 0.18 | 102 | 0.2657 |  |  | -382.0071 | -195.9561 | -1067.6232 | 0 | -832.013 | -2477.5994 | 4 | -309.74 | -82.2528 | -391.9928 | 0.2 | -3344.8073 | -98.7034 | -3443.5107 | 159 | 15 | -1161.54 | -308.448 | -1469.988 | -4506.35 | -407.15 | -4913.5
| Bed Room 2 | 127 | 1168.4 | 2 | 101.29 | 0.0526 | 9.11 | 0.3 | 0 | 0.18 |  | 0.2657 |  |  | -382.0071 | -195.9561 | 0 | 0 | 0 | -577.9632 | 4 | -309.74 | -82.2528 | -391.9928 | 0.2 | -1065.2439 | -98.7034 | -1163.9472 | 54 | 15 | -1161.54 | -308.448 | -1469.988 | -2226.78 | -407.15 | -2633.93
| Bed Room 3 | 111 | 1021.2 | 2 | 101.29 | 0.0526 | 9.11 | 0.3 | 0 | 0.18 |  | 0.2657 |  |  | -382.0071 | -195.9561 | 0 | 0 | 0 | -577.9632 | 4 | -309.74 | -82.2528 | -391.9928 | 0.2 | -1065.2439 | -98.7034 | -1163.9472 | 54 | 15 | -1161.54 | -308.448 | -1469.988 | -2226.78 | -407.15 | -2633.93
| Bed Room 4 | 132 | 1214.4 | 2 | 110.4 | 0.0526 | 0 | 0.3 | 0 | 0.18 | 132 | 0.2657 |  |  | -416.3648 | 0 | 0 | 0 | -1076.7227 | -1493.0874 | 5 | -387.18 | -102.816 | -489.996 | 0.2 | -2256.3209 | -123.3792 | -2379.7001 | 110 | 15 | -1161.54 | -308.448 | -1469.988 | -3417.86 | -431.83 | -3849.69
[5 empty] | 110.4 | 0.22 | 0 | 0.3 |  | 0.18 |  | 0.2657 |  |  | -1741.4496 | 0 | 0 | 0 | 0 | -1741.4496 | 0 | 0 | 0 | 0 | 0.2 | -2089.7395 | 0 | -2089.7395 | 97 | 0 | 0 | 0 | 0 | -2089.74 | 0 | -2089.74
| Bed Room 5 | 117 | 1076.4 | 2 | 110.4 | 0.22 | 0 | 0.3 | 0 | 0.18 |  | 0.2657 |  |  | -1741.4496 | 0 | 0 | 0 | 0 | -1741.4496 | 4 | -309.74 | -82.2528 | -391.9928 | 0.2 | -2461.4275 | -98.7034 | -2560.1309 | 119 | 15 | -1161.54 | -308.448 | -1469.988 | -3622.97 | -407.15 | -4030.12
| Bed Room 6 | 142 | 1306.4 | 2 | 110.4 | 0.22 | 0 | 0.3 | 0 | 0.18 |  | 0.2657 |  |  | -1741.4496 | 0 | 0 | 0 | 0 | -1741.4496 | 5 | -387.18 | -102.816 | -489.996 | 0.2 | -2554.3555 | -123.3792 | -2677.7347 | 124 | 15 | -1161.54 | -308.448 | -1469.988 | -3715.9 | -431.83 | -4147.73
| Corridor | 208 | 1913.6 | 0 | 27.6 | 0.0526 | 0 | 0.3 | 126.96 | 0.18 | 69 | 0.2657 |  |  | -104.0912 | 0 | -701.581 | 0 | -562.8323 | -1368.5045 | 7 | -542.05 | -143.9424 | -685.9924 | 0.2 | -2292.6654 | -172.7309 | -2465.3962 | 114 | 0 | 0 | 0 | 0 | -2292.67 | -172.73 | -2465.4
|  |  | 0 |  | 18.4 | 0.22 | 0 | 0.3 |  |  |  | 0.2657 |  |  | -290.2416 | 0 | 0 | 0 | 0 | -290.2416 | 0 | 0 | 0 | 0 | 0.2 | -348.2899 | 0 | -348.2899 | 16 | 0 | 0 | 0 | 0 | -348.29 | 0 | -348.29
| Toilet 1 | 38 | 349.6 | 0 | 78.2 | 0.0526 | 0 | 0 | [6 empty] | -294.925 | 0 | 0 | 0 | 0 | -294.925 | 1 | -77.44 | -20.5632 | -98.0032 | 0.2 | -446.8381 | -24.6758 | -471.5139 | 22 | 0 | 0 | 0 | 0 | -446.84 | -24.68 | -471.52
| Toilet 2 | 38 | 349.6 | 0 | 0 | 0.0526 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -77.44 | -20.5632 | -98.0032 | 0.2 | -92.928 | -24.6758 | -117.6038 | 5 | 0 | 0 | 0 | 0 | -92.93 | -24.68 | -117.61
| Toilet 3&6 | 55 | 506 | 0 | 103.96 | 0.0526 | 0 | 0 | [6 empty] | -392.0768 | 0 | 0 | 0 | 0 | -392.0768 | 2 | -154.87 | -41.1264 | -195.9964 | 0.2 | -656.3362 | -49.3517 | -705.6879 | 33 | 0 | 0 | 0 | 0 | -656.34 | -49.35 | -705.69
| Toilet 4 | 36 | 331.2 | 0 | 0 | 0.0526 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -77.44 | -20.5632 | -98.0032 | 0.2 | -92.928 | -24.6758 | -117.6038 | 5 | 0 | 0 | 0 | 0 | -92.93 | -24.68 | -117.61
| Toilet 5 | 41 | 377.2 | 0 | 78.2 | 0.0526 | 0 | 0 | [6 empty] | -294.925 | 0 | 0 | 0 | 0 | -294.925 | 1 | -77.44 | -20.5632 | -98.0032 | 0.2 | -446.8381 | -24.6758 | -471.5139 | 22 | 0 | 0 | 0 | 0 | -446.84 | -24.68 | -471.52
2nd floor | Bed Room 7 | 98 | 882 | 2 | 98.89 | 0.0526 | 9.11 | 0.3 | 92 | 0.18 |  |  | 98 | 0.0461 | -372.9557 | -195.9561 | -508.392 | -323.9263 |  | -1401.2301 | 3 | -232.31 | -61.6896 | -293.9996 | 0.2 | -1960.2481 | -74.0275 | -2034.2756 | 94 | 15 | -1161.54 | -308.448 | -1469.988 | -3121.79 | -382.48 | -3504.27
| Bed Room 8 | 98 | 882 | 2 | 98.89 | 0.0526 | 9.11 | 0.3 | 27.6 | 0.18 |  |  | 98 | 0.0461 | -372.9557 | -195.9561 | -152.5176 | -323.9263 |  | -1045.3557 | 3 | -232.31 | -61.6896 | -293.9996 | 0.2 | -1533.1988 | -74.0275 | -1607.2263 | 74 | 15 | -1161.54 | -308.448 | -1469.988 | -2694.74 | -382.48 | -3077.22
| Storage | 65 | 585 | 2 | 145.39 | 0.0526 | 9.11 | 0.3 | 27 | 0.18 |  |  | 65 | 0.0461 | -548.3268 | -195.9561 | -149.202 | -214.8491 |  | -1108.3339 | 2 | -154.87 | -41.1264 | -195.9964 | 0.2 | -1515.8447 | -49.3517 | -1565.1964 | 72 | 15 | -1161.54 | -308.448
| Living area | 225 | 2025 | 8 | 116.89 | 0.0526 | 9.11 | 0.3 | 117 | 0.18 |  |  | 225 | 0.0461 | -440.8413 | -195.9561 | -646.542 | -743.7083 |  | -2027.0476 | 8 | -619.49 | -164.5056 | -783.9956 | 0.2 | -3175.8452 | -197.4067 | -3373.2519 | 156 | 60 | -4646.16 | -1233.792 | -5879.952 | -7822.01 | -1431.2 | -9253.21
|  | 0 | 0 |  | 126 | 0.22 | 0 | 0.3 |  | 0.18 |  |  | 0 | 0.0461 | -1987.524 | 0 | 0 | 0 |  | -1987.524 | 0 | 0 | 0 | 0 | 0.2 | -2385.0288 | 0 | -2385.0288 | 110 | 0 | 0 | 0 | 0 | -2385.03 | 0 | -2385.03
| Dining 1 | 439 | 3951 | 18 | 36 | 0.0526 | 0 | 0.3 | 125.12 | 0.18 |  |  | 439 | 0.0461 | -135.7711 | 0 | -691.4131 | -1451.0574 |  | -2278.2417 | 15 | -1161.54 | -308.448 | -1469.988 | 0.2 | -4127.738 | -370.1376 | -4497.8756 | 208 | 135 | -10453.86 | -2776.032 | -13229.892 | -14581.6 | -3146.17 | -17727.77
|  |  | 0 |  | 98.89 | 0.0526 | 9.11 | 0.3 | 0 | 0.18 |  |  | 0 | 0.0461 | -372.9557 | -195.9561 | 0 | 0 |  | -568.9118 | 0 | 0 | 0 | 0 | 0.2 | -682.6942 | 0 | -682.6942 | 32 | 0 | 0 | 0 | 0 | -682.69 | 0 | -682.69
| Toilet 7 | 38 | 342 | 0 | 55.2 | 0.0526 | 0 | 0 |  |  |  |  | 38 | 0.0461 | -208.1824 | 0 | 0 | -125.6041 |  | -333.7864 | 1 | -77.44 | -20.5632 | -98.0032 | 0.2 | -493.4717 | -24.6758 | -518.1476 | 24 | 0 | 0 | 0 | 0 | -493.47 | -24.68 | -518.15
| Toilet 8 | 38 | 342 | 0 | 55.2 | 0.0526 | 0 | 0 |  |  |  |  | 38 | 0.0461 | -208.1824 | 0 | 0 | -125.6041 |  | -333.7864 | 1 | -77.44 | -20.5632 | -98.0032 | 0.2 | -493.4717 | -24.6758 | -518.1476 | 24 | 0 | 0 | 0 | 0 | -493.47 | -24.68 | -518.15
| Toilet storage | 38 | 342 | 0 | 81.88 | 0.0526 | 0 | 0 |  |  |  |  | 38 | 0.0461 | -308.8039 | 0 | 0 | -125.6041 |  | -434.4079 | 1 | -77.44 | -20.5632 | -98.0032 | 0.2 | -614.2175 | -24.6758 | -638.8934 | 30 | 0 | 0 | 0 | 0 | -614.22 | -24.68 | -638.9
| Total | 2203 |  | 44 | [10 empty] | -13119.4936 | -1567.6488 | -3917.2709 | -3434.2794 | -2471.568 | -24510.2607 |  | -5652.84 | -1501.1136 | -7153.9536 |  | -36195.7209 | -1801.3363 | -37997.0572 | 1758 | 330 | -25553.88 | -6785.856 | -30869.748 | -59072.24 | -8229.43 | -67301.67
Notes
Heating temperature of air is 90°F and room set point is 70°F
Occupancy for bedroom - 50 sft/person or actual
As per Wisconsin 364 ventilation rate shall be 7.5 cfm/person
2 persons are considered for each bedroom